GSM Remote Monitoring

#### Operating and installation instructions

#### GC 055

GSM, GPRS Programmable Communicator

Transmits input conditions/Controls outputs

Measures analogue data

Access control system/Dallas chips

Audio input / output

Contents

Contents	3

1.	Caution	4

2.	Safety	4

3.	Description	4

4.	Technical Parameters	5

5.	Design	5

5.1.	Assembly accessories and optional extras	6

5.2.	Dimensions	6

5.3.	Front panel	6

6.	Connection of inputs - outputs	7

6.1.	Connection to the upper row of connectors	7

6.2.	Connection to the lower row of connectors	7

7.	Installation - Configuration	8

7.1.	Installing the SIM card	8

7.2.	LED Indicators	8

7.3.	Connecting via PC	8

7.4.	Control Panel	9

8.	SMS - editing configuration - control	9

9.	Maintenance	11

Warranty conditions	12

Warranty certificate	14

# Caution

GC 055 is a device for wireless data transmission, its activity may affect other electronic devices that are prone to interference. The functionality of GC055 can also be affected by sources of electromagnetic interference (contactors, relays) located near the device.

Only qualified personnel may install or repair this product. The device is not waterproof. Operation is possible only in a dry environment.

Disclaimer:

Use of the GC 055 communicator is at the discretion of the user. LEVEL Ltd. shall not be liable for any damage arising from the use of this communicator.

# Safety

We recommend you follow these tips in order to prevent damage to property or injury to persons. Do not install or use in areas where the use of radio equipment is forbidden.

Installation and configuration can only be performed by qualified personnel, or a person who has sufficient knowledge of this equipment and its safety requirements. All related (connected) devices, PC, power supply and peripherals must be in accordance with the requirements of the EN 60950-1 standard.

Place the unit so that the LEDs are visible to the operator. These LEDs provide information about the operating modes and status. In the case of equipment failure, switch off and call the qualified personnel. The power switch should be installed in the vicinity.

# Description

GC 055 Communicator is a compact alarm, monitoring and control unit for electronic devices with SMS, GSM / GPRS communication and the possibility to control by calling.

The unit is programmed using a PC and software control panel via a USB connector. It has 8 analogue inputs (one internal which monitors the supply voltage), 3 outputs - open collector transistor (two outputs and two inputs are connected in parallel), one power relay (230 V / 5 A), one LED light on the panel controlling the programme, Dallas bus to connect readable access chips / cards, thermometers and A/D converters.

Examples of use:

GSM detector - conveys information about changes of input state via SMS

GSM home alarm - alarm with GSM communicator

GSM remote control - such as opening gates by ringing

Access identification system - using the Dallas chips for registering attendance

Measurement and control of analogue values

The reading of consumption meters and status via SMS / GPRS

# Technical Parameters

| Power supply | 10 to 24 Vss / 1A, power consumption <30 mA at 12 V |
| --- | --- |
| GSM | 850, 900, 1800, 1900 Mhz SIM card Plug-in 1,8 V (only the newest type) Antenna connector GSM - SMA |
| Communication | Calling, SMS, CSD data, GPRS |
| SMS | Outgoing SMS alarm SMS queries the status of digital and analogue inputs SMS configuration change SMS launch on operators behalf |
| CSD data (modem connection) | Edit configuration Reading measured values Reading the event memory Control of outputs Upgrade firmware |
| GPRS connection | GPRS Class 10 support for static and dynamic IP and VPN UDP protocol, security option - AES 128-bit All functions such as CSD data |
| Memory report | Flash 512 kB |
| 8x analogue inputs 4x outputs 2x LED outputs 1x Dallas input | Input max. 30V DC (1 × internal voltage measurement) Output current up to 0.5 A The ability to control the configuration Max. length of cable - 100 m |
| USB | Mini USB for connecting to PC - configuration, upgrade firmware |
| Real time clock RTC | Date and time battery back up |
| Protection class | IP 20 |
| Measurements | 52 x 90 x 57 mm |
| Weight | 150 g |
| Design | Plastic - attachment at TS 35 DIN-rail |
| Working temp. range | -25 to +65 °C |

# Design

The GC 055 design is in a plastic box suitable for mounting on a TS 35 DIN-rail. If the GC 055 is placed in a metal cabinet, the GSM antenna must extend outside the cabinet. The antenna cable can not be adjusted. If the length of the antenna is insufficient, order an antenna with a longer cable.

## Assembly accessories and optional extras

| Accessories included with GC 055 |
| --- |
|  | GC 055, GSM antenna 3dB SMA magnet 5m cable |
| Accessories which can be purchased |
| SA 012 830 CB 170 020 ED 060 500 ED 060 550 ED 060 100 | Power adapter for DIN rail (10-14VDC / 1,25 A) 1.5 module width Mini USB cable Identification reader for Dallas chips Dallas identification chip Dallas temperature sensor (-40 to 130°C) |

## Dimensions

## Front panel

The front panel of GC 055 is equipped with seven LED indicators. The 'Action' LED is controlled by the configuration. The 'GSM' LED indicates the GSM status (Section 7.2).

LED Out 1-4 indicates state of output - the LED is lit when the output is active, the output is earthed.

# Connection of inputs - outputs

## Connection to the upper row of connectors

The top part of GC 055 is equipped with an SMA type GSM connector. If the GC 055 has a metal casing, then the GSM antenna should be outside the enclosed space.

From the Dallas bus it is possible to simultaneously connect up to 10 input devices (thermometers, A/D converters) and an unlimited number of readable access chips. It is necessary to maintain the polarity of the connected device.

Inputs 1-5 are analogue voltage with a measuring range of 0 to 30V DC maximum.

## Connection to the lower row of connectors

The lower part is equipped with connectors for connecting a supply voltage in the range between 12-24V DC.

Outputs in the active state are earthed (log. 0). The maximum allowable output current is 0.5 A. The auxiliary relay to the output is for connecting against the (+) terminal of the power supply. Output 4 may be the same as GC 075 and fitted with an internal relay. Load capacity of the relay is 230V / 5 A.

Outputs 1 and 2 can be used as analogue inputs No. 6 and 7

# Installation - Configuration

## Installing the SIM card

Before inserting the SIM, disconnect the power to GC 055.  Inserting the SIM card into the device whilst in use is not advised.

Use the notches on the sides of the front panel and a suitable tool (weak screwdriver) to gently pry open the cover of the front panel. Open the SIM card holder using slight pressure in the direction of the arrow (open). Place the SIM into the open door of the holder so that the notch on the SIM matches the recess in the substrate holder. Close the SIM card holder and secure with gentle pressure in the direction of the arrow (close). The SIM card must not be locked with a PIN or the account frozen by the provider.  It must also have sufficient credit, all SMS erased and an activated GPRS data service.

## LED Indicators

| GSM – Yellow LED |
| --- |
| 0,5 s / 0,5 s 1× short / 10 s 1× short / 4 s 1× short / 2 s 2× short / 10 s 2× short / 4 s 2× short / 2 s | No GSM signal or no SIM card Low power mode – No GPRS context Normal power mode – No GPRS context Moving to low power mode – No GPRS context Low power mode – Linked to GPRS Normal power mode – Linked to GPRS Moving to low power mode – Linked to GPRS |
| ACTION – Red LED |
|  | Controlled by the configuration |
| POWER – Green LED |
| 1× short / 2 s | Power on |
| OUT – Yellow LED |
|  | On = active output (output is earthing, relay closed) |

## Connecting via PC

GC 055 is designed to be connected to a PC via mini USB connector located under the front panel cover. Before connecting GC 055 to a PC you must download the driver for this device. The required software is downloadable from the manufacturer's website (www.levelna.cz - 'Downloads'). When connected to a PC, GC 055 will Install the device to the PC. In Windows, Device Manager should check the COM port on which GC 055 communicates with the PC and then use the software control panel. Detecting the COM port is also possible using Level Finder from the software package Level Utility. It is advisable to always use the same USB connection when connecting GC 055 to the PC.  Using a different USB will be a change the COM port.

## Control Panel

Control panel is a software tool for configuring the product line GC 05x and GC 07x and allows you to view the current status and  download the report.

The installed device and PC must be connected in CP - Connection - Gallery connections to create connections through the COM port.  In the Gallery connection, select 'New' and name this connection.  Then click on 'Next', select 'Local Area Connection', click 'Next' and select the COM port to which the device communicates with the PC.  Finally, click 'Finish'.

# SMS - editing configuration - control

Via SMS you can't create a new configuration for the device, but only edit the existing configuration for the device (eg phone number in the phone book). For a list of available SMS commands, see the software Help Control Panel in the Appendices. Setup and operation is done through SMS messages sent to the phone number of the SIM card in the communicator.

Sample SMS:

PASSWORD command1 parameter1 command2 parameter2 command3 parameter3 command4 parameter4

PASSWORD		maximum 8 characters a-z and 0-9. Factory setting is ‘picola‘.

space

COMMAND		command name for the desired configuration

space

PARAMETER	              value? for enquiry or. (full stop) to delete values

One SMS message can contain up to 4 commands with parameters. The communicator will confirm the execution of commands by sending an SMS. Lower and upper case letters are only distinguished in the password.

For remote access to GC 055 via GPRS it is necessary to set the APN (Access Point Name) to connect to the Internet.

| Setting the APN provider |
| --- |
| SMS Reply Value x Set password x | password APN x APN „x“ apn provider - |
| Setting the access point name APN - only for selected foreign providers |
| SMS Reply Value x Set password x | password GPRSNAME x gprsname „x“ APN login name - |
| Setting APN password - only for selected foreign providers |
| SMS Reply Value x Set password x | password GPRSPSW x gprspsw „x“ Password for APN - |

| SMS to establish a GPRS connection |
| --- |
| SMS Reply | password CALLR @IP_adresa,port,UDP,1 CALLR @IP_adresa,port,UDP,1 |

After receiving the SMS GC 055 will send UDP packets to the IP address and port.  The IP address must be a fixed and public, routeable port to the PC where the conenction is to be made. The port must be enabled in the firewall on the PC. In the Control Panel, you need to wait for connections on the appropriate UDP port. For settings and procedures, see the software Help Control Panel.

| Changing the password |
| --- |
| SMS Reply Value x Set password x | password PSW x psw x new password – maximum 8 characters a-z and 0-9 picola |

| Launch action |
| --- |
| SMS Reply | password name of action name of action |

Via SMS you can run any action in the configuration.

| Query the status of analogue inputs |
| --- |
| SMS Reply | password ains ains ain1= 0.00;ain2= 0.00;ain3= 0.00;ain4= 0.00;ain5= 0.00;ain6= 0.00;ain7= 0.00;power=11.64 the voltage at the input [V] |

| Query the status of outputs |
| --- |
| SMS Reply | password outs outs out1=1,out2=1,out3=1,out4=1,led1=1, output value is given binary (0 = connected to ground, the relay is closed, LED lit) |

# Maintenance

The GC 055 Communicator requires no maintenance. We recommend regular monitoring of the external backup battery for 1 year if the battery is installed.

Update Firmware and configuration.

On www.levelna.cz in 'Downloads' you will find the current version of the firmware and the Control panel. Unzip the downloaded file and save to disk. In the Control Panel establish a connection with the communicator via USB cable CB 170020, modem - data connection or via GPRS and perform the firmware update. Before you upgrade firmware, we recommend that you backup your configuration.

## Warranty conditions

The warranty period is 24 months from date of purchase.

Warranty repairs will be made within ten working days from receipt of the defective goods in LEVEL, provided that the spare parts are in stock. If not, the user will be offered an alternative solution until the repair is completed.

Warranty repairs will be carried out in the company and the warranty period shall be extended by the duration of the repairs. The manner of return transport will be determined by our service technician.

No warranty is given in the case of loss or replacement of the warranty, or if the product is damaged by natural disaster, during transport, improper placement, improper use, if the device in used in unsuitable conditions, or in the case of removing or breaking the sealing labels.

The warranty does not apply to consumables - batteries, ink ribbons, etc.. It does not apply to faults caused by installed software or interference. The company is not responsible for any losses arising from device failure.

The warranty does not apply to malfunction due to external conditions such as changes in legislation, changes in GSM networks, changes of power supply, etc.

The warranty applies after submitting a fully completed warranty card and a device for repair, including accessories. A duplicate warranty will not be issued, the customer is responsible for its accuracy and originality.

## Warranty certificate

| Name of Product : | Type : |
| --- | --- |
| Serial number : | Date of purchase: |

Distributor :

Address, telephone No., stamp :

Signature:

| Accepted for repair | Despatch date | Description of fault |
| --- | --- | --- |

# GC 055  @ 1.03 © 2011

LEVEL s.r.o., Plhovská 1997, Náchod 547 01

e-mail: level@levelna.cz